Pipeline RTD temperature probes （TM1111)(1)

Applications：

The Pipeline RTD temperature probes are used to measure the temperature of pipe wall or round surface. It can be fixed with cable ties. Heat paste can be used to strengthen heat conduction. It is recommended to adopt measurements of heat preservation and insulation in case direct heat radiation affects the measure accuracy.

Technical data

Connecting cable:  Silicone, temperature range:-50℃~+180℃

Teflon, temperature range -50℃~+260℃

Glass Fiber, temperature range:-50℃~+350℃

Protection tube:    Stainless steel 304/316

Sensor element:    Pt100, Pt500, Pt1000 meets IEC 751

Tolerance :        Class B: △t=±(0.30 + 0.005 |t| )℃

Class A: △t=±(0.15 + 0.002 |t| )℃

接线图 Wiring diagram 铂电阻 RTD

单支2线 1x2-wire单支3线 1x 3-wire 单支4线 1x4-wire

双支4线 2x4-wire 双支6线 2x6-wire

白色芯线 white core wire 红色芯线 red core wire

Dimensions(外形尺寸图）

Order Details:

| TM1111 | — | 25 | — | 50 | — | (3) | — | (4) | — | (5) | — | (6) | / | (7) |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

- R

R will be determined by customers’s requirements.

- Sensor element

- 11      1 x Pt100 in 2-wire circuit

51      1 x Pt500 in 2-wire circuit

- 61      1 x Pt1000 in 2-wire circuit

13      1 x Pt100 in 3-wire circuit

14      1 x Pt100 in 4-wire circuit

12      2 x Pt100 in 4-wire circuit

16      2 x Pt100 in 6-wire circuit

62      2 x Pt1000 in 4-wire circuit

- Measuring range/Connecting cable

13    -50℃ ～+ 180℃/Silicone

14    -50℃ ～ +260℃/Teflon

15    -50℃ ～ +350℃/Glass Fiber

- Cable length L（L≥100mm）

- 100     100mm

200     200mm

2000    2000mm

Note:other lengths as per customers’ requirements.

(100mm≤L<1000mm, L1=50mm, L≥1000mm, L1=100mm)

- Additional options

- 00      No

01      Strain relief spring/strain relief spring hose

99      Special options

List the additional options in sequence, separated by commas.