Form J Push-in RTD temperature probes （TM1401)

Applications:

HVAC, Refrigeration equipments, Experimental facilities, Mechanical equipments, Ovens,Water tanks.

Technical data

Protection tube：stainless steel 304/316

Sensor element:    Pt100, Pt500, Pt1000 according IEC 751

Tolerance :     Class B: △t=±(0.30 + 0.005 |t| )℃(standard)

Class A: △t=±(0.15 + 0.002 |t| )℃

Protection Class： IP54 or IP65

Response time：t0.9  approx. 14secs, in water 0.2 m/sec, diameter 6mm

接线图 Wiring diagram 铂电阻RTD

单支2线 1x2-wire

单支3线 1x 3-wire

双支4线 2x4-wire

单支4线 1x4-wire

安装螺钉 mounting screw

红色标记 red mark

Dimensions

Order Details:

| TM1401 | — | (1) | — | (2) | — | 000 | — | (4) | — | (5) | — | (6) | / | （7） |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

- (1)protection tube diameter D

4       4mm

5      5mm

6       6mm

8       8mm

9       9mm

11      11mm

- Insertion length EL

- 50     50mm

- 100    100mm

- 150      150mm

- 1000     1000mm

Note: other lengths as per customers’ requirements.

- (4) Sensor element

11     1 x Pt100 in 2-wire circuit

12     2 x Pt100 in 4-wire circuit

13     1 x Pt100 in 3-wire circuit

14     1 x Pt100 in 4-wire circuit

51     1 x Pt500 in 2-wire circuit

61     1 x Pt1000 in 2-wire circuit

62     2 x Pt1000 in 4-wire circuit

(5)Measuring range

20    -50℃ ～+ 400℃

(6) Cable length L（L≥100mm）

100     100mm

200     200mm

2000    2000mm

Note: other lengths as per customers’ requirements.

(100mm≤L<1000mm, L1=50mm, L≥1000mm, L1=100mm)

(7)Additional options

00      No

01      strain relief spring/strain relief spring hose

02      shielded connecting cable

07      Ferrules as per DIN 46 228 part 4(standard)

08      Multipole connector (providing types)

99      Special options

List the additional options in sequence, separated by commas.