Spring cutting sleeve RTD temperature probes（TM1407)

Applications:

Gear cases, steam turbines etc.

Technical data

Protection tube：stainless steel 304/316

Sensor element:  Pt100, Pt500, Pt1000 meets IEC 751

Tolerance :     Class B: △t=±(0.30 + 0.005 |t| )℃(standard)

Class A: △t=±(0.15 + 0.002 |t| )℃

Protection Class： IP54 or IP65

Response time：t0.9  approx. 14secs, in water 0.2 m/sec, diameter 6mm

接线图  wiring diagram 铂电阻RTD

单支2线 1x2-wire双支4线 2x4-wire单支3线 1x3-wire

单支4线 1x 4-wire安装螺钉 mounting screw红色标记 red mark

Dimensions（外形尺寸图）

Order Details:

| TM1407 | — | (1) | — | (2) | — | (3) | — | (4) | — | (5) | — | (6) | / | （7） |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |

(1)protection tube diameter D and d

4       4mm

5       5mm

6       6mm

8       8mm

9       9mm

11      11mm

（2）Insertion length EL

50     50mm

100    100mm

150      150mm

Note: other lengths as per customers’ requirements

- Process connection G

123   M16 x 1.5

213    G1/2

Details in “Threaded code table”

(4) Sensor element

11     1 x Pt100 in 2-wire circuit

51     1 x Pt500 in 2-wire circuit

61     1 x Pt1000 in 2-wire circuit

13     1 x Pt100 in 3-wire circuit

14     1 x Pt100 in 4-wire circuit

12     2 x Pt100 in 4-wire circuit

16     2x Pt100 in 6-wire circuit

62     2 x Pt1000 in 4-wire circuit

(5)Measuring range

20    -50℃ ～+ 400℃

(6) Cable length L（L≥100mm）

100     100mm

200     200mm

2000    2000mm

Note: other lengths as per customers’ requirements

(100mm≤L<1000mm, L1=50mm, L≥1000mm, L1=100mm)

(7)Additional options

00      No

02      shielded connecting cable

07      Ferrules as per DIN 46 228 part 4(standard)

08      Multipole connector (providing types)

99      Special options

List the additional options in sequence, separated by commas.